# GOVERNMENT OF NAGALAND

DEPARTMENT OF NEW & RENEWABLE ENERGY

REVISED DETAIL PROJECT REPORT ON

DEVELOPMENT OF 5MW SOLAR POWER PV PLANT
AT HOVUKHU, NIULAND

MARCH 2023

Detailed project report (DPR) of 5 MW Solar Crystalline Silicon

Technology based grid-connected Power Plant in Nagaland

HOVUKHU, NIULAND: 5 MW

SOLAR PV POWER PLANT

EXECUTIVE SUMMARY

Nagaland is located in north-eastern part of India and is well endowed with the abundant renewable energy resources. However, the State faces energy deficit due to under-utilized renewable energy resources. Nagaland is primarily dependent on Central Generating Station (CGS), located in other parts of north-east, for meeting its energy needs. With an objective to reduce the State’s dependence on CGS, this project is envisaged as a pioneer solar project for providing clean energy to the people while ensuring energy security.

In order to meet the country’s climate commitments, and to achieve energy security, India has an ambitious renewable energy targets to be achieved by 2030. The country’s declaration during the Climate Week in New York in 2019 have set a target of installing 450 GW of renewable energy capacity in the country. The State in tandem with the country’s vision and target has proposed to come up with this ambitious project to be taken up in the state.

The Department of New & Renewable Energy (DNRE) had proposed for developing 5 MW Solar Power Plant at Hovukhu Village under Niuland District resulting in the preparation of a DPR  for development of the Solar Power Plant.

The Revised DPR has been prepared with a project estimated cost of Rs 25.05 crores at March, 2023 price level.

I am highly indebted and thankful to the officers and staff involved in preparation of this DPR.

KOHIMA							         		Er. KIMABA

MARCH 2023				                            			     Director

Table of Contents

Glossary

Abbreviations

Project at Glance …………………………………………………………….……...………..1

Section 1: Site Assessment............................................................................................2

Section 2: Solar Radiation Resource Assessment ........................................................8

Section 3: Solar PV Technologies..................................................................................14

Section 4: Solar PV System............................................................................................20

Section 5: Estimation of Annual Electric Output ............................................................41

Section 6: Project Implementation Schedule..................................................................49

Section 7: Cost Estimation and Conclusion....................................................................54

Annexure – I   : Meeting Minutes of Land Allotment

Annexure – II  : Site Map of Hovukhu

Annexure – III : Tariff Calculation

Glossary

Direct solar radiation: It is the solar radiation propagating along the line joining the receiving surface and the sun. It is also referred as beam radiation. It is measured through Pyrheliometer.

Diffuse solar radiation: It is the solar radiation scattered by aerosols, dust and molecules. It does not have a unique direction and also does not follows the fundamental principles of optics. It is measured by shading Pyranometer.

Global solar radiation: The global solar radiation is the sum of the direct and diffuse solar radiation and is sometimes referred to as the global radiation. The most common measurements of solar radiation are total radiation on a horizontal surface often referred to as ‘global radiation’ on the surface. It is measured by Pyranometer.

Irradiance: Irradiance is the rate at which radiant energy is incident on a surface, per unit area of surface.

Albedo: It is essentially the ratio of reflected to incident light. The Albedo of an object is a measure of how strongly it reflects light from light sources such as the Sun.

Abbreviations

AC – Alternate Current

a-Si - Amorphous Silicon

ACSR- Aluminum Conductors Steel Reinforced

BOO- Build Own Operate

BOS- Balance Of the System

c-Si – Crystalline Silicon

°C - Degree Celsius

CERC – Central Electricity Regulatory Commission

CdTe - Cadmium Telluride

CO2 -Carbon Dioxide

COD- Commercial Operation Date

CT -Current Transformer

DC – Direct Current

DPR - Detailed Project Report,

EIA - Environmental Impact Assessment

EPA - Energy Purchase Agreement

GoI- Government of India

GSS- Grid Sub-Station

HT- High Tension

IAM -Incidence Angle Modifier

IEC - International Electro-technical Commission

IEC 61646 - IEC standard code for PV module performance

IEC 61730 – IEC standard code for product safety

IFC - International Finance Corporation

IP65 - International Protection Rating / Index Protection: classifies the degrees of protection provided against the intrusion of solid objects (including body parts like hands and fingers), dust, accidental contact, and water in electrical enclosures.

IREDA – Indian Renewable Energy Development Agency

ITPI – IT Power India Pvt. Ltd.

ITPG - IT Power Group

Km – Kilometer

KV – Kilovolt

KVA – Kilovolt Ampere

KWh – Kilowatt Hour

KWp – Kilo Watt peak

LCC - Life cycle costs

MCB Main Combiner Box / Miniature Circuit Breaker

MMS Module Mounting Structure

MNRE – Ministry of New and Renewable Energy

MVA – Mega Volt Ampere

MW – Megawatt

MWh – Megawatt Hour

NASA – National Aeronautics and Space Administration – US space agency

NASA-SSE – NASA Surface meteorology and Solar Energy

NISE National Institute of Solar Energy

NREL National Renewable Energy Laboratory

NOC - No Objection Certificate

O&M - Operation and Maintenance

PLF/ CUF Plant Load Factor/ Capacity Utilization factor

PPA Power Purchase Agreement

PSA Power Sale Agreement

PCB – Pollution Control Board

Poly-Si - Polycrystalline silicon PV - Solar Photovoltaic

RPO – Renewable Purchase Obligation

PT Power Transformer

PV Photo Voltaic

RfS REC Request for Selection Rural Electrification Corporation

SLDC State Load Dispatch Centre

SPD Solar Power Developer

STU State Transmission Utility

VCB Vacuum Circuit Breaker

STC – Standard Test Conditions of 1000 W/m2 irradiance, Air mass 1.5, 25 °C cell temperature.

T-Line – Transmission line

UV – Ultra Violet

V - Voltage

Wp – Watt peak

XLPE Cross Linked Polyethylene

PROJECT AT GLANCE

| Sl No. | Particulars | Description |
| --- | --- | --- |
| 1 | Project site | Hovukhu Village |
| 2 | District Name | Niuland |
| 3 | Name of the State | Nagaland |
| 4 | Global Solar Irradiance on horizontal Surface | 4.63 kWh/m2 /day |
| 5 | Solar PV Module Technology | Advance Monofacial PERC Full Cell |
| 6 | Type of System | Ground mounted (Fixed) |
| 7 | Type of PV Module Considered for the system | Contendre Greenergy Pvt. Ltd. CG M72-400WP |
| 8 | Proposed Capacity | 5 MW |
| 9 | Projected Module Area required | 25125 m2 |
| 10 | Capacity of each Module Proposed | 400 Wp |
| 11 | Inverter Capacity Central Inverter. | 5 x 1000 kW AC |
| 12 | Projected Net Energy Production Per year | 8.76 GW/hr |
| 13 | Total Project Cost | Rs. 2505 Lakhs |
| 14 | Debt Equity Ratio | 70:30 (70 Debt : 30 Equity) |
| 15 | Levellised Tariff | Rs 3.97 per KWh |
| 16 | Project Owner | DNRE |
| 17 | Name of the Customer of Power | Government of Nagaland |

Section-1

Site Assessment

Hovukhu (25° 58' 48"N and 93° 57' 0"E) is located under Niuland District of Nagaland, which was under erstwhile district of Dimapur. Dimapur is located at 25°54′45”N and 93°44′30”E. A large area of the district is in the plains with an average elevation of 260 meters above sea level excepting the Medziphema Sub-division and few villages in Niuland Sub-division, which are located in the foothills. It has well road and rail connectivity from Guwahati, the gateway of northeastern India. The Department of New and Renewable Energy Nagaland is planning to develop a solar energy power project based on grid interactive system at Hovukhu Village under Niuland District. Initially, the Asian Development Bank (ADB) has prepared a Pre Feasibility Report (PFR) for the development of project at Ganeshnagar Industrial Estate and engaged Meghraj Consultants for preparation of DPR on Viability Gap Funding (VGF) mode for the development of Solar Park. The identified technology was Si Mono Cell; while the capacities of proposed power plant was 12MW in Ganeshnagar.

Figure 1. District Map of Dimapur, Nagaland

The Hovukhu site is located in a semi-developed non-forest area as shown in the figure below on an area comprising agricultural farms and residential habitats, on a plot designated for Solar Farm. As per the Forest maps published by the Nagaland GIS and Remote Sensing Centre, none of the sites is in forested area. The site has nonetheless thick vegetation on the land that would need to be cleared before construction of the solar power plant.

Land

Hovukhu

The proposed project area lies at Hovukhu Village under Niuland. Most of the area of is covered by thick vegetation. The state Government of Nagaland had allotted 50 acres of land to DNRE for proposed 5 MW Solar Park Project.

For the geographical location of Nagaland, the distance between rows or pitch required yields 1.93 m for each 1 meter length of PV module, which means that 1 MW of PV modules mounted in a fixed tilt at 26o with 19% efficiency requires 0.6 hectares-Assuming that DC oversize may go up to 20% with required area for the inverters, internal roads, control room, switching yard and avoidance of shading as well as land usage, it was considered 1.8 hectares per MW as being sufficient to guarantee enough land for the development of a PV plant even with less efficient modules, but also not to allow too low efficient PV modules to be considered.

Furthermore, all sites were analysed in terms of the topography and in particular the slopes. The feasible area of each plot took into consideration only areas with slopes lower than 10% from east to west and facing south. Slopes towards the north were not considered, neither southwest nor southeast. These sizes are considered to be a minimum to be developed, but not a constraint for SPDs that would like to develop more capacity and utilize more area. The maximum capacity is linked with the evacuation capacity per plot. A new dedicated 33/11kv transmission line has been considered to evacuate power from the solar power plant to the existing Niuland Sub-station. The analysis of the selected site is presented below along with the evaluation and feasible area.

Connectivity:

Airport

Niuland is served by the Dimapur airport which is located in the 3rd mile (AH-1). It is the only civil airport in the state and operates routes to Kolkata, Guwahati, Imphal and Dibrugarh.

Railway

Dimapur is the only city in Nagaland that is connected by Rail and Air. There are direct train services to cities like Guwahati, Kolkata, New Delhi, Bangalore, Chandigarh, Amritsar, Dibrugarh and Chennai from Dimapur railway station. The station is categorised as an A category railway station under the Northeast Frontier Railway.

Road

To reach Dimapur by road is an excellent option as the city is well connected with major cities by road. The road network is well linked with Kohima and Peren district of the state. There is very good network of city roads also where all modes of vehicular transport communications operate. There are several highways passing through Dimapur both international and national; Asian highway-AH1 and AH2, National highway NH29, NH129, NH129A. All Weather Road from Dimapur to Niuland is 33.9kMs.

Water Availability

In PV power plants water is required only for cleaning of the PV modules. The location has water access through groundwater which is available at 40 feet and a bore well exist on the half-finished structure far from the proposed site. The water requirement will be met by groundwater abstraction. There is also a running stream within the vicinity of the project area which can be pumped for use in project.

Power Evacuation Facility

Power evacuation is an essential part of any power generation project. As the end user is generally located far from the project location where the bulk power is generated, there is a need for the proper evacuation planning to ensure that the same is optimal – both operationally and cost-wise. This requires detailed review and analysis of the existing transmission network in the vicinity of the project sites to identify suitable interconnection points to connect the proposed evacuation system with the existing system. While doing so, there is a need to consider the following elements:

- Optimal sizing of the equipment and lines to ensure evacuation capacity and cost optimisation;

- Technical feasibility of the proposed arrangement;

- Topography of the land through which the line is proposed to be passing including presence of forests, valleys, etc. in the path of the line;

- Land related issues like availability of land for the transmission lines and sub-stations, possible Right of Way (RoW) issues, etc.

Under a normal situation, the generated power is taken to nearest suitable power substation at suitable voltage, considering all the factors involved for the efficient and economical way for the evacuation to enable transmission of the same to the intended users. As mentioned earlier, the sites selected for the proposed Solar Power PV Plant is spread out across areas with Hovukhu around which the sites are located.

An estimated generation to the tune of 5 MW has been proposed to be established in this area. There is an existing sub-station near the proposed Hovukhu Solar plant site.

The electricity generated through solar PV power plant is proposed to feed in to grid.  The power may be evacuated at 33 kV from the solar plant and feed to the 33 kV bus at Niuland Grid sub-station with a 33 kV overhead single circuit line of 8 km approximately. In addition, a 33 kV incoming bay shall be constructed at the 33 kV Hovukhu S/S for which space is available at the existing substation.

The details of the substation is given below.

Figure no: 3

Fig 4. Power Evacuation Network of the Project

Section – 2

Solar Radiation Resource Assessment

The electrical output of a PV plant is dependent on the solar radiation it receives. Outside the Earth’s atmosphere, on a surface normal to the solar beam, the power density is 1,365W/m2. As the solar radiation passes through the atmosphere, some of it is scattered and absorbed, the amount depending on the length of the atmospheric path traversed by the solar radiation and the quantity of dust, water vapour, ozone, carbon dioxide and other aerosols and gases present. About one half of the scattered energy is returned to the earth as diffused radiation from the sky. The diffused radiation plus the direct irradiance from the sun are together termed as total irradiance. The total irradiance on a horizontal surface is called the global irradiance. The diffused sunlight can vary from about 20% on a clear day to 100% in heavily overcast conditions.

The peak irradiance of 1,000W/m2 has been taken as the standard value by which PV modules are rated. Hence, a 5 MW PV Power plant will generate 5 MW of electricity in an irradiance of 1000W/m2 and a cell temperature of 25oC and Air Mass 1.5. However, the total solar energy received in a day over a specific area is more important than the instantaneous solar irradiance. This is called daily solar irradiance or insolation and is expressed as kWh/m2 /day. The solar resource is not equally available in all regions of the world. On a clear day in the tropics, when the sun is overhead, the global irradiance can exceed 1000W/m2 but in high latitude it rarely exceeds 850W/m2. Similarly, daily solar insolation may be 5-7kWh/m2 /day in the tropics but could be less than 0.5kWh/m2 /day in high latitudes. The solar insolation for the site is found to be 1620kwh/m2 per year.

Historically, climatological profiles of insolation and meteorology parameters calculated from ground measurements have been used for determining the viability of Renewable Energy Technology (RET) projects. These climatological profiles are used for designing systems that have low failure rates. Although ground measurement data has been used successfully in the past for implementing RETs, there are inherent problems in using them for resource assessment. Ground measurement stations are located throughout the world, but they are situated mainly in populated regions. In remote areas (where many RETs are implemented) measurement stations are limited.

Also, at any particular station, data recording can be sporadic leading to incomplete climatological profiles; and, data inconsistencies can occur within a station and from one station to another. In contrast to ground measurements, the Surface meteorology and Solar Energy (SSE) data set is a continuous and consistent 22-year global climatology of insolation and meteorology data on a 1° by 1° grid system. Although the SSE data within a particular grid cell are not necessarily representative of a particular microclimate, or point, within the cell, the data are considered to be the average over the entire area of the cell. In utilizing the SSE data set, an estimate of the renewable energy resource potential can be determined for any location on the globe. That estimate is considered to be accurate enough for feasibility studies of new renewable energy projects.

Solar Radiation over India

India being a tropical country is blessed with good sunshine over most parts, and the number of clear sunny days in a year also being quite high. India’s equivalent solar energy potential is about 6,000 million GWh of energy per year. Being a tropical country, India is blessed with good sunshine over most parts, and the number of clear sunny days in a year also being quite high. India is in the sunny belt of the world. The country receives solar energy equivalent to more than 5,000 trillion kWh per year.

The daily average global radiation is around 5 .0 kWh/m2 in north-eastern and hilly areas to about 7.0 kWh/m2 in western regions and cold dessert areas with the sunshine hours ranging between 2,300 and 3,200 per year. In most parts of India, clear sunny weather is experienced for 250 to 300 days a year. The annual global radiation varies from 1600 to 2200 kWh/m2. The estimated capacity using solar PV technology is estimated to be around 20 MW/km2.

Figure 5 & Figure 6 below shows the Global Horizontal Irradiation (GHI) in India, mapped by National Renewable Energy Laboratory (NREL). This component of the solar irradiation is the relevant one for photovoltaic systems. MNRE/SECI has deployed a network of solar measurement stations through NIWE across the country to validate the solar irradiation potential and build a bankable database for PV projects in the country. The map of those stations is also shown below. The available station is Nagaland is in Kohima.

Solar Irradiation and Weather Data

The location chosen for the analysis of the environment data:

- Hovukhu: 25° 58' 48"N and 93° 57' 0"E

Using NASA database the following parameters were obtained:

- Global Horizontal Irradiation(GHI)

- Air temperature

- Wind speed

- Relative humidity

- Precipitation

Table 3: Environment data and daily average for Hovukhu Village

Solar Irradiation Resource Assessment

The data obtained from NASA presented above was compared with other sources to verify its accuracy. The map from Solar GIS showing the GHI throughout India is presented below.

Figure 2.3: GIS map of India from Solar GIS

Fig 7. Solar Irradiation Map of India from Solar GIS

According to Solar GIS a value around 1620 kWh/m2 is provided, that is higher than the value by NASA. According to the atlas from NIWE the following irradiation data is provided for the proposed site.

The GHI values for the site is found to be around 1620 kwh/m2 per year based on solar resource assessment provided by Solar GIS. Similarly, as per the Atlas from National Institute of Wind Energy (NIWE), the irradiation value is 1587 and 1591. Accordingly, a PV plant at the site will be able to generate 1620 kwh/kw in the site with a 10% to 15% DC over AC capacity.

Section – 3

Solar Photovoltaic Technologies

Solar Photovoltaic (SPV) technology is primarily a solid-state semiconductor- based technology, which converts a fraction of the incident solar radiation (photons) in to direct electricity. PV system can deliver electric energy to a specific appliance and/or to the electric grid. Photovoltaic systems are flexible and modular; hence the technology can be implemented on virtually any scale size, connected to the electricity network or used as standalone or off grid systems, easily complementing other energy sources. PV offers several advantages viz;

⇒ Complementarierities with other energy resources; both conventional and Renewable

⇒ Flexibility towards implementation and

⇒ Environmental advantages.

The Solar Sector

The solar sector worldwide has shown a dynamic unsurpassed by any other source of power, being it conventional or renewable. Solar in 2018 continued to dominate the newly built with more than coal, gas and nuclear combined with 102 GW. Not only due to the speed of construction, but also to the price. Figure 9 below shows the installed capacity per generation source.

The real reason behind such success is the cost, which continues to decrease to historical levels and with an enduring resilience. Solar power has achieved a cost reduction trend never seen in any other generation source. It now challenges all other sources in terms of cost and no longer requires any subsidies or state aids. All regions on Earth are looking at solar and how to add it to their generation mix. The graph below shows the cost decrease of electricity per source since 2009 with the feed-in tariffs still dominating renewables to 2018. 2019 is showing the same levels or even slightly lower.

Figure 9. Installed power worldwide in 2018 per type

Figure 2: Cost decrease of power generation (source: Lazard 2018)

The levelized costs of electricity per source of generation are shown below in Figure 10 where again the leadership of solar in terms of costs is clear.

Figure 10: LCOE costs in 2018 for power generation technologies (source: Lazard 2018)

Solar has come of age and in the last years has surpassed all goals with the rise of Asia and namely China leading the pack with an astonishing pace. In the last three years saw a capacity addition of 50% of the current total, mostly coming from China.

PV has grown tremendously in the past years as shown. According to IRENA2 at the end of 2018 a total of 485 GW of solar power is installed worldwide, being close to 480 GW in solar PV. Asia continued to dominate the global solar capacity expansion, with a 64 GW increase in 2018. Three countries accounted for most of this growth, with increases of 44 GW in China, 9.2 GW in India and 6.5 GW in Japan. China for the first time did not account for half of all new solar capacity installed in 2018. Other inclusions from relevant regions included: USA (10.5 GW), Europe (9 GW) and Australia (4 GW).  In 2017 China with 130 GW Japan with almost 49 GW Germany with 42 GW USA with 41 GW and Italy with close to 20 GW were the top 5 worldwide solar markets. However, India has already overtaken Italy in 2018 with 26.9 GW of installed capacity and USA overtook Germany with 49.6 GW to be now in third. The huge growth of solar worldwide is also mirrored on the growth of Renewables in general as is well demonstrated in the graph below with a steady and consistent yearly growth.

Installed Solar Capacity in India

The Government of India has committed to have 40% of the electricity generation in the country from non-fossil fuel based resources by the year 2030. Supporting that target the Government has announced 100 GW by 2022, of which 40 GW from Solar Parks, 40 GW from solar rooftops and the rest from other type of solar plants.

India became a beacon in relation to solar power with a massive goal, 5 times the previous objective of the National Solar Mission. Furthermore, implemented Solar Parks in an unprecedented way and leading the world on such development. Rajasthan, Andhra Pradesh are paving the way for solar to reach costs and penetration levels that were only mirages in India just some years ago. The graphs below show the expected trajectory for solar demand in India and also what is happening on the ground with a massive capacity of projects under development.

Fig 11. Solar Energy Demand Trend (MERCOM India)

Installed Solar Capacity in Nagaland

There is no utility scale solar capacity installed in Nagaland. The RPO obligations are being met and Nagaland leads in implementation, being one the number of states that has fulfilled at least 60%of the RPO obligations. For financial year (FY) 2018-2019 the solar RPO is set at 6.25 percent and non-solar RPO at 10.75 percent. The solar RPO for FY 2021-2022 is 10.5 percent and non-solar RPO is 10.5 percent.

State Level Policy Interventions

The states have also come out with state specific policies to encourage establishment of the RE based generating stations in the states. Similarly, the Regulators have also specified the RPO that the distribution companies in the state have to adhere to as a part of the overall power procurement plan to meet the power demand in the state. Details of some of the policies / regulatory interventions in the State of Nagaland are mentioned below for reference.

Solar Energy Policy

The State of Nagaland does not have any Renewable Energy or Solar Energy policy in place as of now.

Renewable Purchase Obligations in Nagaland

The Nagaland Electricity Regulatory Commission (NERC) has notified the Nagaland Electricity Regulatory Commission (Renewable Purchase Obligation and its Compliance) Regulations, 2011 for notifying the Renewable Purchase Obligation and its Compliance through promotion of generation and purchase of power from renewable sources at specified tariff. The Regulations specify the minimum quantum of electricity to be purchased by the licensees from renewable energy sources expressed as percentage of their total consumption of electricity in a year. The targets specified in the Regulations are as follows:

- FY 2010-11: 6%

- FY 2011-12: 7%

- FY 2012-13: 8%

It is also specified that for subsequent years, the Commission will separately specify the purchase obligation as the Commission deems fit, provided that 0.25% percentage point out of the total consumption shall be procured from generation based on solar as renewable energy source only. These Regulations are applicable to the Distribution Licensees and also to any other person consuming electricity of 1MW and above:

(i) Generated from conventional Captive Generating Plant for his own use and/or; (ii) procured from conventional generation through open access / third party sale.

The Regulations also specify that the Renewable Energy Certificates shall be the valid instruments for the discharge of the mandatory obligations set out in these regulations for the obligated entities to purchase electricity from renewable energy sources. No subsequent amendments to the Regulation are available which mention about any revision in the RPO for future years.

The above obligation encourages the licensee and other obligate entities to procure part of their entire power requirement through renewable power sources.

Accordingly, there are number of interventions at the National and State Level which encourage the setting up of the solar power plants and hence provide impetus for development of Solar Parks which could house such solar projects. Further, guidelines have also been issued by the Ministry of New and Renewable Energy, Govt. of India in the matter of encouraging development of Solar Park in the country. The lists of these guidelines which are applicable to the present project also are elaborated in the subsequent section.

SECTION - 4

Components Solar PV Plant

A PV system essentially consists of modules (array of solar cells generating the electricity) and a balance of system (BoS) including the cabling, battery, charge controller and DC/AC inverter, as well as other components and support. Most of the systems are in flat-plate (having a fixed orientation) variety but these might be use sun-tracking (single or double axis) concentrators in order to achieve high radiation on a small area and hence higher efficiency.

The storage system (batteries) is not required in grid connected SPV systems. Solar PV module is the smallest PV unit that can be used to generate substantial amounts of PV power. Although individual PV cells produce only small amounts of electricity, PV modules are manufactured with varying electrical outputs of direct current (DC) electricity.

.

Grid Connected Solar PV Systems.

Grid connected solar systems offer a unique opportunity to silently and cleanly generate significant amounts of energy, which are designed to operate in parallel with, and interconnected, with the electric utility grid. A grid-connected solar electricity system links several solar panels together through several central inverters to the power grid.

Grid connected solar power plant comprises of the main equipment and components listed below.

• Solar PV Modules

• Central inverters

• Module Mounting system

• Grid connect equipment

• Monitoring system

• SCADA

• Cables & connectors

A simple block diagram, related to the interconnection of various systems for grid connectivity, is shown in Fig.12 below for reference. The power from modules is directed to the central inverters through the DC combiner boxes and from the inverters it is routed though the Low voltage panel to the transformer. From the transformer, the high voltage power is routed to the metering panel and eventually to grid through the High

Figure 12: Block Diagram Showing Interconnection of Various Systems

Solar PV Modules

Solar cells represent the fundamental power conversion unit of a photovoltaic system, which has much in common with other solid-state electronic devices, such as diodes, transistors and integrated circuits. For practical operation, solar cells are usually assembled into modules. Its operation is based on the ability of semiconductors to convert sunlight directly into electricity by exploiting the photovoltaic effect. In the conversion process, the incident energy of light creates mobile charged particles in the semiconductor, which are then separated by the device structure and produce electricity.

A photovoltaic module is a packaged interconnected assembly of photovoltaic cells, which converts sunlight into energy. For this project Generic mono crystalline PV Technology solar module 400Wp has been considered.

Single/Mono-crystalline Silicon Solar Cell.

This is the most established and efficient solar cell technologies till date, which have the module efficiency of 15-21%. The cell and module fabrication technology is well developed and reliable. These cells are manufactured from single silicon crystal, by process called Czochralski process. During the manufacturing, c-Si crystals are cut from cylindrical ingots, they do not completely cover a square solar cell module.

A single solar or PV cell is an integrated group interconnected from cell to cell constitutes a SPV module as shown below in Figure 13.

Figure 13: Mono Crystalline solar cell and Module

There are several SPV module manufacturing/supply firms approved by Ministry of New & Renewable Energy (MNRE), Government of India. Technical parameters of SPV modules from Contendre Greenergy Pvt. Ltd. is depicted below in Figure 14 & Figure 15 for reference and or comparison.

Fig 14: SPV Module Technical Parameters/Specifications

Fig 15: SPV Module Technical Parameters/Specifications

(The above table is for the purpose of reference only)

Inverters

After modules inverters are the most important components in a solar power system. In recent years inverter technologies have been developed significantly and numbers of reputed companies are now offering high efficiency inverters. Because of technical improvements in circuit design and integration of required control and protection circuits into control circuits cost, size and weight of inverters has reduced significantly. The control circuits provide sufficient control and protection features like maximum power generation, frequency and power factor controller. Inverter technology is very important to have reliable and safety grid interconnection. Inverters connecting a PV system to public grid are to be purposefully designed that allows power transfer to and from the grid. Many a times inverters can be connected in “master- slave” criteria, when the succeeding inverter switching on when enough solar radiations are available or in case main inverter malfunctions. The standard voltage and frequency for single circuit is 220 V and 50 Hz.

Inverter is the heart of a solar power project. It is also known as Power Conditioning Unit (PCU). A PCU consists of an electronic Inverter along with associated control, protection and data logging devices. Typically the utility scale inverters are unidirectional and supply the power to the grid in the form of AC power conforming to IEC 61727 or equivalent standard. The inverter has a feature that it automatically adjusts with the grid conditions such as the voltage & frequency levels to suit the Grid.

Inverter and Control

Grid interconnection of PV systems is accomplished through the inverter, which converts DC power generated from PV modules to AC power used for ordinary power supply for electric equipments. It is also required to generate high quality power to AC utility system with reasonable cost. To meet with these requirements, up to date technologies of power electronics are applied for PV inverters. By means of high frequency switching of semiconductor devices with PWM (Pulse Width Modulation) technologies, high efficiency conversion with high power factor and low harmonic distortion power can be generated. The microprocessor based control circuit accomplishes PV system output power control. The control circuit also has protective functions, which provide safety grid interconnection of

PV systems. The inverter output always follows the grid in terms of voltage and frequency. This is achieved by sensing the grid voltage and phase and feeding this information to the feedback loop of the inverter. Thus, control variable then controls the output voltage and frequency of the inverter, so that inverter is always synchronized with the grid.

Software controlled Maximum Power Point Tracking (MPPT) techniques are utilized in the control system to optimize the solar energy fed into the grid. The control system detects if the insolation level is above a predetermined value and the grid supply is within the preset limits in voltage and frequency, the inverter modules synchronise and connect to the grid supply and proceed to export the available solar energy. The control unit will automatically disconnect from the grid if the grid voltage or frequency moves out of its operating range. Also, the unit will switch over to a low power sleep mode at night and during periods of low insolation and automatically wake up, when the insolation level rises above a preset point. Once the grid is back into its operating range, the inverter unit will synchronize and connect to the grid to export all the available energy generated by the PV array. The inverter will be based on power MOSFET transistors with very low resistance in the output stage and a toroidal transformer with ultra-low hysteresis losses and also provide galvanic insulation between the DC and AC side.

The controller will have following control and automated functions.

⇒ Inverter start up, shut off and disconnection sequence

⇒ Over / under voltage & frequency protection

⇒ Anti islanding protection

⇒ Power tracking to match inverter to the arrays

⇒ Adjustment of delay periods to customize system shutdown sequence

⇒Graphical user interface for real time communications, monitoring and control ⇒ Optional remote monitoring via internet modem

⇒ Faults notification via modem

⇒ Data acquisition and logging

⇒ DC monitoring

Power Evacuation System

Grid interactive PV system has the advantage of more effective utilisation of generated power. However, the technology requirement of both from the utility and PV system side need to be safeguarded for effective utilisation of system. Safety and reliability of system could be accomplished through inverter systems.

The main components of solar PV grid interactive power plants are.

⇒ Solar modules or array

⇒ Interconnecting Wiring

⇒ Inverter to convert DC voltage to AC voltage

⇒ Step up transformer

⇒ Control cum monitoring system

⇒ Earthing and lightening protection system

Grid Connected Solar PV Systems.

Grid connected solar systems offer a unique opportunity to silently and cleanly generate significant amounts of energy, which are designed to operate in parallel with, and interconnected, with the electric utility grid. A grid-connected solar electricity system links several solar panels together through a central inverter to the power grid.

Fig 16: Schematic SPV grid connected power

Every Grid Power solar system comes with a solar panel array, a grid connected inverter, a roof mounting assembly, a pre-wired circuit breaker distribution board and all warning and emergency procedure signage. The output from a photovoltaic module is proportional to available solar irradiance and therefore it is dependent upon the location, time of day and climatic conditions. A single unit cannot be relied upon without a back-up source of power or energy storage.

The primary component in grid-connected PV systems is the inverter, or power-conditioning unit (PCU), which converts the DC power produced by the solar array into AC power consistent with the voltage and power quality requirements of the utility grid.

Schematic representation of SPV grid connected power plant is shown in Figure 16 above.

Array Support Structure (MMS)

Modules shall be mounted on a non-corrosive support structure suitable for site condition (extreme site conditions to be taken account) with facility to adjust tilt to maximize annual energy output. The structure will be designed for simple mechanical and electrical installation. It shall support SPV modules at a given orientation, absorb and transfer the mechanical loads to the ground properly. The frames and legs of the array structures shall be made MS hot dip galvanized/ anodized aluminum of suitable sections of angle, channel, tubes or any other sections as may deemed fit conforming to national/ international standards for steel structure to met the design criteria. Minimum thickness of galvanization should be at least 120 microns. All nuts & bolts will be made of very good quality stainless steel. The minimum clearance between the lower edge of the modules and the developed ground level shall be 800 mm.

In addition, the material of the structure is to be selected in such a way that it serves at least for 25 years. In general, “galvanized steel” is used to make the structures. The mounting structures shall be designed as per the soil and wind conditions at the site. The array structure shall be so designed to withstand storm condition with wind speed up to maximum 160Kmph to 170kmph. The support structure design & foundation shall also be designed to withstand wind speed applicable for the site conditions. Nut & bolts, supporting structures including Module Mounting Structures shall have to be adequately protected from atmosphere and weather prevailing in the area.

Cables and Accessories

The size of the cables between array interconnections, array to junction boxes, junction boxes to PCU etc. shall be so selected to keep the voltage drop and losses to the minimum. Aluminum cables will be used from junction box to power the conditioning unit. These wires are insulated with a special grade PVC compound formulated. The skin coloration offers high insulation resistance and long life.

Cables are flexible & of annealed electrolytic grade copper conductor, confirm to IS 1554/694-1990, extremely robust and resist high mechanical load and abrasion. Cables are also high temperature resistant and have excellent weather proofing characteristics which provide a long service life. The connectors/lugs of copper material with high current capacity and easy mode of assembly are proposed.

Junction Boxes

A) Terminal Box

Terminal box is a part of a PV module, from which output is taken. Each PV module is provided with one bypass diode in the terminal box.

B) Series Junction Box (SJB)

One series junction box is provided for each series mounting structure for taking out final output. A blocking diode connected in series with 25 modules in this box.

Blocking Diodes

These diodes are connected in series with string of PV modules and its functions are as follows:

⇒ Prevent circulating current between PV module strings.

⇒ Prevent reverse flow of current from battery through PV array

during night and/or periods of low insolation.

Bypass Diodes

⇒These diodes are connected in reverse direction (anode to negative of PV module and cathode to positive of PV module) across each PV module of the string. They have the same current rating as that of blocking diodes and their operation is as follows:

Under normal operating conditions, the bypass diodes are reverse biased and play no part. When any module in a series string is shadowed, the current through the module is reduced. Under these circumstances, the PV module gets reverse biased leading to power dissipation across the module and reduction in output power of which is undesirable. Presence of bypass diode provides an alternate path to flow of current in the string (as the diode becomes forward biased when PV module gets reverse biased) and also limits dissipation by limiting the voltage across PV module to typically 0.7V.

C) Array Junction Box (AJB)

These are for paralleling various series junction box (SJB) outputs. Terminal blocks are provided in the array junction box for paralleling +ve & -ve electrical output

D) Main Junction Box (MJB)

Main junction boxes used to connect the output of array junction boxes to the grid tide inverter. The output of AJB’s is fed in to one main junction box. The output of main junction boxes works as an input for inverter.

Data logger

The data logger takes care of data monitoring and regular data logging of the SPV system. The data logger also allows user to perform monitoring and logging of multiple connected PCU’s. Once the system is configured real time data can be obtained and displayed. Following data from the system are logged and displayed.

- Solar radiation

- Ambient temperature

- Module temperature

- DC voltage

- DC current

- DC power

- Grid voltage, frequency, current

- Inverter voltage, frequency, current

- Line pf, line KW, Total KW

- Energy exported

The logger will store the above data on to the load side regularly where this data can be printed and used for scrutiny of system performance and evaluation.

Safety Requirements

Islanding

The condition of a Distributed Generation (DG) generator continuing to power a location even though power from the Electric utility is no longer present is termed a “islanding”. Islanding of inverter-connected PV-generator systems means any situation where the source of power from the network operator’s distribution system is disconnected from the network section in which the generator is connected, and one or more inverters maintain a supply to that section of the distribution system or consumer’s installation. The situation may cause an electrical shock hazard to service personnel operating on the islanding network section while it has been supposedly shut down, by separating it from the main power station. Islanding can be dangerous to Utility workers, who may not realize that the utility is still powered even though there's no power from the Grid. For that reason, Distributed Generators must detect Islanding and immediately stop producing power.

To prevent islanding, the Power Conditioning Unit has to disconnect quickly (within a few second) in response to failures on the immediate distribution line. To provide this safety function, voltage, frequency and current have to be monitored and in case of exceeding the limit, the system has to trip. A disconnect switch which is accessible to only utility people is recommended. When the power plant is disconnected from the Grid it will supply power for captive use.

Lightning and Over Voltage Protection

The SPV Power plant shall be provided with Lightning and over voltage protection connected to proper earth mats. The main aim of over voltage protection is to reduce the over voltage to a tolerable level before it reaches the PV or other sub-system components. The source of overvoltage can be lightning or other atmospheric disturbance. The Lightning Conductors shall be made as per applicable Indian or International Standards in order to protect the entire Array Yard Lightning stroke. Necessary concrete foundation for holding the lightning conductor in position will be made. The lightning conductor shall be earthed through flats and connected to the Earth mats as per applicable Indian/International Standards with earth pits. Each Lightning Conductor shall be fitted with individual earth pit as per required Standards including accessories, and providing masonry enclosure with cast iron cover plate having locking arrangement, watering pipe using charcoal or coke and salt.

Earthing System

Each Array structure of the SPV Yard shall be grounded properly. The array structures are to be connected to earth pits as per Indian/International standards. Necessary provision shall be made for bolted isolating joints of each earthing pit for periodic checking of earth resistance. The earth conduction shall run through appropriate pipes partly buried and partly on the surface of the control room building. The complete earthing system shall be mechanically & electrically connected to provide independent return to earth.

Codes and Standards

All equipments of the PV power plant shall conform to international standards including IEEE for design and installation of grid connected PV system. The standards cover various aspects such as PV modules, cable types and selection, temperature considerations, voltage ratings, BOS wiring, inverter wiring, blocking diodes, bypass diodes, disconnect devices, grounding requirements, surge and transient suppression, load centre, power qualities, protection features and safety regulations.

Monitoring System.

System proposed will maintain and provide all technical information on daily solar radiation availability, hours of sunshine, duration of plant operation and the quantum of power fed to the grid. This will help in estimation of generation and number of other generation parameter of array capacity installed at the site. The system also enables diagnostic and monitoring functions for these components.

Communication: Features of Data modem (analogue/Ethernet) are as follows.

• Monitors the performance of the entire power plant (string wise monitoring, junction boxes, inverters, etc.)

• Evaluates (strings, inverter, nominal/actual value), quantity of DC Power & AC Power produced

• Measures instantaneous irradiation level and temperature at site. It also measures the module back surface temperature

• Alerts in case of error (discrepancy in normal operation of components, like module string/ diodes/ inverter/ junction box / loose contacts/ etc.) to facilitate recognition and correction of the fault with minimum downtime

• Visualizes nominal status of the connected components via Control Center PC Software (diagnosis on site or remote)

• Logs system data and error messages for further processing or storing

• Stores and visualizes energy yield data (for life of the plant) in the Portal from where the data can be accessed remotely.

SCADA System

The instrumentation & control system for the solar power plant is based on the prevailing standard engineering practices. Design will ensure full compliances of codes and standards as applicable the field of instrumentation & control for power plant and the whole plant will be operated through SCADA system.

The SCADA system shall have the following features:

• Monitoring: Ability to control, using specially designed devices, the state &

evolution of one or various physiologic (or others) parameters to detect possible malfunctions

• Remote control: Group of devices which allow modifying the state of the

equipment and devices of the plant, from a remote location

The SCADA system shall be used for the following minimum tasks:

• To invoice the produced energy

• To detect the incidences and malfunctions (up to logical string level)

• To give the information at a given time interval: a) Availability, b) Performance Ratio and Energy Production

• The SCADA System will be reliable and robust and some components need redundancy for trouble free operation.

The major SCADA features incorporated in to the control system are listed below;

⇒ Operator interface of latest technology: Instantaneous grid, array, inverter, AC, and metering of all parameters.

⇒ Integrated AC/DC data point logging: Instantaneous logging of all parameters. Including AC parameters, generator run hours and energy details.

⇒ Fault and system diagnostics with time stamped event logging: Selectable event logging resolution for enhanced diagnostics.

⇒ Remote SCADA features with specific needs of station monitoring and remote communication are to be incorporated. Remote system access software, secured transmission of data and central PC facility will be provided.

System Earthing

The 66kV system will be solidly grounded on the HV neutral terminal of the transformer. The 11kV system will be resistance grounded using the neutral point of the star connected LV winding of the 66/11kV power transformer. This will be designed to limit the earth fault current in the 11kV system to 200A, to limit the damage to equipment and cable in the 11 kV systems in the event of an earth fault. The 415V system will be solidly grounded at the LV winding neutral terminals of the load centre transformer.

In-house Power

The internal electric power demand of the photo voltaic power plant mainly consists of lighting and small power loads in the 66kV switch yard, Including the control and administrative building and road lighting. It is proposed to meet this power demand by availing HT connection to an ancillary transformer from the power department. During night times, when there is no generation in the photovoltaic modules, it is possible to switch off the main power and load centre transformers, thereby eliminating the power loss in the plant distribution network at night. The 66kV sub-station, control and administrative building, roads etc. will be provided with artificial lighting with appropriate level of illumination in different areas. Stale of the art energy efficient tamps and luminaries will be used to provide uniform, glare-free lighting.

Water System

The plant water requirements will be predominantly for cleaning of solar arrays and personnel use. Water is envisaged to be obtained from ground water bore wells. The estimated total capacity required for the proposed plants are presented below considering 2 to 3litres per m2 and an efficiency of the PV modules of 19.33%.

Estimated Water requirements for the MWac capacities per site.

| Site | MWac min | Litres/m2 per washing |  | 1 time per month (KL/day) |  |
| --- | --- | --- | --- | --- | --- |
|  |  | 2 | 3 | 2 | 3 |
| Hovukhu | 5 | 47052 | 70578 | 1.44 | 2.32 |

The proposed Bore wells with an estimated yield of 5 KL/D will be sufficient to supply the required water. Since the water is stated to be hard, necessary arrangement for softening water will be required for cleaning of modules to avoid formation of scaling on the module surface. This water cannot be used to clean the solar modules. A water filtration Plant may be constructed to filter the hard water to be used for cleaning the modules.

An Overhead Tank (OHT) arrangement with a capacity of 12KL to store the water required for washing panels is also incorporated in the plan.

Section-5

Estimation of Annual Electrical Output

Mono-Crystalline Full Cut Solar Cells have been identified suitable PV technology for proposed location which could perform effectively under the climatic and operating conditions at Hovukhu Village under Niuland District, Nagaland.

Energy Generation

The annual energy yield for the proposed PV power plant is defined as the amount of energy fed into the grid after due consideration of all kinds of generation and distribution losses. The solar PV based power plant comprises of optical energy input (which is essentially dependent on the geographical/ seasonal/ climatic and operating parameters with time) and electrical output (which depends on the technical specifications of electrical appliances in use).

Energy Generation Assessment The proposed 5 MW solar PV plant is expected to generate about 8.76 MU of energy in the first year of operation at a net CUF of 20% at the metering point. Thereafter annual degradation factor of 1.5% for first year and 0.75% thereafter in production has been considered for mono crystalline modules for financial calculations. The energy yield has been calculated based on array surface considering south facing (i.e. zero azimuth angles). The expected plant production for different probability scenarios (probability of meeting a generation value) is presented below:

S.No.      Technical Losses                                               Values

1           Incident Angle Modifier                                            -1.35%

2           Soiling Loss factor                                                   -4.0%

3           Module Degradation Loss (For Year#1)                 -0.2%

4           PV loss due to irradiance level                                -0.62%

5           PV loss due to temperature                                     -8.02%

6           Module quality loss                                                  -0.3%

7           Module array mismatch                                           +2.0%

8           DC Ohmic wiring loss                                              -1.07%

9          Inverter loss during operation                                   -1.86%

10          Auxiliary Loss 						  -0.4%

11	     System Unavailability      					  -2.0%

12          AC Ohmic loss                                                         -0 %

13           External Transformer Loss 				  - 2.0%

The plant’s Capacity Utilization Factor (CUF)/ Plant Load Factor (PLF) has been calculated using the following formula:

CUF = Energy Generation/ (Installed Capacity x 365 x 24) ------ (1)

Capacity Utilization Factor is defined as “the relationship between actual output that is produced with the installed equipment, and the potential output which could be produced with it, if capacity was fully used.” The capacity utilization for the project adopted is 20%.

PR = Energy Generation / (Plant Capacity x Global Tilted Radiation) ------ (2)

The Performance Ratio (PR) is a measure of the performance of a PV plant at a given irradiation level. The PR has been calculated using the following formula:

Yield Factor

Yield factor is defined to be a factor consolidating all the system losses that are occurring across this power plant. The major losses that occur during the operation of the solar PV power plant are temperature loss, module mismatch loss, DC to AC conversion losses.

Temperature Losses

Whenever there is increase in ambient temperature, the temperature of the PV module also increases, resulting in reduction of power output from the PV module. This depends on the temperature coefficient of the PV module as specified by the manufacturer. A loss of 10.4% is expected with the increment in ambient temperature at the project site from standard conditions.

Module Mismatch Losses

The maximum power output of the total PV array is always less than the sum of the maximum output of the individual modules. This difference is a result of slight inconsistencies in performance from one module to the next and is called module mismatch. Maximum 1-2% losses will be there for module mismatch, but the modules will be connected in series and parallel after testing to match the properties. This will be keeping the mismatch losses to 1%.

DC to AC Conversion Losses

The DC power generated by the solar module must be converted to AC power using an inverter. Some power is lost in the conversion process. In this case as discussed before that selected inverter has maximum DC power into AC power conversion efficiency of 98%.

Yield factor is the multiplication of the typical coefficients for all these losses occurring across the module up to the transformer output in this photovoltaic power plant. It helps in estimating the totally generated units that can be evacuated into the grid.

Hovukhu: Niuland  5 MW

No of Modules:   12500 (400 Wp) Contendre Greenergy Pvt. Ltd. CG

M72-400

No of inverters:   5x1000kW (ABB PVS800/SUNNY CENTRAL 1000CP XT)

Area of Module:  25125 M2

No of strings    :  500 Strings

No of array	      :  25 in series

The project has been modeled and assessed with available tools and accordingly simulation was performed with available datas using RETscreen & PVsyst from which the results are tabulated below.

Overall Solar Power Plant Performance Summery: Hovukhu, Niuland

(Based on Simulation conducted in the same location)

Section - 6

Project Implementation Schedule

Based on international practices and technological advancements, it is assumed that project will be supplied, installed & commissioned in 10 months from the date of sanction. Loan repayment period has been considered as 15 years after the commissioning of project.

System Description

The Solar electricity is produced when the Photos from the sun rays hit the electrons in the Solar PV panels, this will generate Direct Current (DC). The DC electricity from the panels passes through DC distribution network to a grid-interactive inverter, which converts the DC electricity into Alternating Current (AC) by using state of the art technology by IGBT methodology and fed through A/C distribution system linked to the electricity supplied by the grid AC. The Inverters will synchronize with the utility power with respect to the Voltage and frequency of Grid, the Voltage is further stepped up to the grid voltage of the Utility generally 33kV/66kV/132kV/220kV in India.

Indicative Scope of Work

1. Electrical

⇒ Supply, fitting, fixing of Solar PV Modules with appropriate module mounting structures and frames as per specification including overall planning and design of the power plant.

⇒ Design and construction of appropriate foundation base for holding the

module mounting structure with supply of all requisite materials, excavation, concreting, back filling, shoring and shuttering, etc.

⇒ Supply and installation of Junction boxes of appropriate standards with

required Protection and Isolation system

⇒ Design, Supply and Installation of AC Power Conditioning Units with all

protection and controlling arrangement as per specification e.g. 250 kW, 3 Ph, 50 Hz, 415 V, 4 wire or a suitable mix of PCUs to get the desired performance. String monitoring and MPPT features are included.

⇒ Interconnection of PCUs, transformer LT side, LT switchgear, with appropriate cables and associated materials including supply materials.

⇒ Design, manufacture, supply, installation, interconnection and interfacing of Computer Aided Data Acquisition Unit as per specification.

⇒ Supply, installation complete earthing as required for AC & DC power system, PCU, LT switchgear, transformer, all metallic cubicles, HT switchgear with materials as required as per relevant standards.

⇒ Providing Earth Mat and Interconnection of array structures with earth pits in the PV Array Yard.

⇒ Design, fabrication, supply, installation of LT power interfacing panel to evacuate power to the Grid through PCUs with appropriate capacity circuit breakers, isolators, indicators, metering arrangement with selector switch, CTs, PTs and copper busbars as per requirement, in complete. This is assuming upto 3km distance to the nearest substation.

⇒ Design, fabrication, supply and installation of plant monitoring desk to monitor the status of all major equipment through SCADA system including connection to all major equipment and status to be monitored.

2. Control Room and Others

⇒ Electrical wiring in the control room and array yard with supply of cables and wires, switch board, switch, JB, distribution board for lights, fan, exhaust fan, power point for both 5A and 16A

⇒ Supply and installation of lightening arrestors for the control room as per relevant standards.

⇒ Supply, fitting and fixing of CFL lighting fixture, FL lighting fixture, LED lighting fixture for lighting indoor & outdoor various including array yard with required accessories.

⇒ Providing of 5A and 15A plug points in the control room as per requirement.

⇒ Supply, fitting and fixing of ceiling fan, exhaust fan, pedestal fan as per requirement.

⇒Providing of fire extinguisher and sand buckets complying with national/international safety standards.

3. Erection and Installation of Power Evacuation Arrangement

⇒ Erection, supply installation and commissioning of 7.5 MVA transformers 33 Kv/66 KV, 3 phase, 50 Hz with associated switchgear comprising of circuit breakers, isolators, CTs and PTs etc including metering and protection like over current, earth fault, reverse power protection, etc.

4. Civil Works for SPV System

Civil works required for the substation are:

⇒ Topographical survey as per scope already mentioned in technical specifications

⇒ Soil testing as per scope already mentioned in technical specifications

⇒ Planning and design as per scope already mentioned in technical specifications

⇒ Construction of power plant building including control rooms as required, office, amphitheatre, etc.

⇒ Fencing of the site

⇒ Access roads

⇒ Site filling and compaction

⇒ Fences and gates

⇒ Roads and paved areas

⇒ Transformer foundations and oil separator

⇒ Cable channels and ducts

⇒ Control and switchgear building

⇒ Drainage system

⇒ External lightning system

⇒ Foundations for equipment supports, gantries and other steel constructions

⇒ Earthing system

⇒ Air conditioning/heating system in the MV and control room

All buildings shall be equipped with a lightening protection system (LPS). LPS Protection Level I according IEC 61024-1 shall be considered. The building lightening protection system is to be executed, among other standards, according to IEC 61024 and alongside protection of human life, shall prevent damage not only to buildings, but also to electrical and electronic installation.

5. Operation and Maintenance

The operation of solar power plant is relatively simple and restricted to daylight hours in a day. With automated functions of inverter and switchyard controllers, the maintenance will be mostly oriented towards better up keep and monitoring of overall performance of the system. The solar PV system requires the least maintenance among all power generation facility due to the absence of fuel, intense heat, rotating machinery, waste disposal, etc. However, keeping the PV panels in good condition, monitoring and correcting faults in the connected equipment and cabling are still required to get maximum energy from the plant. A maintenance schedule needs to be planned as per service/ guarantee terms of supplier to maintain optimum availability of plant at all times. The maintenance functions of a typical solar PV power plant can be categorised as given below.

Day to day maintenance checks

1. Ensure security of the power plant.

2. Monitor power generation and export.

3. Monitor load centre wise power generation values to detect any abnormality.

4. Entry of unauthorised person, stray animal or migration of birds at the site.

5. Healthiness of fencing and loss of any material from site.

Weekly maintenance checks

1. Inspection of PV panel glass surface clean / wash solar PV panels to free from dust and other dirt like bird’s dropping etc.

Monthly maintenance checks

o Removal of weeds and grass below PV panels and pathways, if any.

o Inspection of solar PV modules and arrays for any damage.

o Check the power terminals for corrosion and proper torque, clean and apply Antioxidant jelly, if necessary.

o Change tilt angle in appropriate months.

Half yearly maintenance checks

o Check all the wiring for physical damage and for any sign of excessive heating.

o Check all the junction boxes for proper covering and sealing.

o Check the fasteners of Solar PV panel mounting structure and array for proper torque and tightening.

Annual maintenance checks

o Check for discoloration of solar PV cells

o Check all the connections and ensure that they ate not loose

o Insulation characteristic checking for the transformer oils

o Checking corrosion, cleaning and painting switch yard structures

o Checks and cleaning of drains and cable trenches in switch yard

o Checking barbed wire fencing for damages and rectifications

Section – 7

Cost Estimation (Financial analysis)

Item of Works:

- Cost for Supply, Installation, Erection and Commissioning of Solar PV Modules.

| Sl. No. | Particulars | Unit | Quantity | Amount (in Rs) |
| --- | --- | --- | --- | --- |
| 1.1 | 400 Wp Mono Crystalline with String Combiner/(Monitoring Box(SMB) – SMB Type 1 – 12 Inputs | MWp | 5 | 14,10,00,000 |
|  | Sub Total |  |  | 14,10,00,000 |
|  | Add GST @18% |  |  | 2,53,80,000 |
|  | Total |  |  | 16,63,80,000 |
| (Rupees Sixteen Crore Sixty Three Lakh Eighty Thousand) only |  |  |  |  |

- Module Mounting Structure (MMS) and Associated Civil Works

| Sl. No. | Particulars | Unit | Quantity | Amount (in Rs) |
| --- | --- | --- | --- | --- |
| 2.1 | Mounting Structure (Galvanised Rafter and Purlins with column posts of H200DG 80 Micron, fixed Tilt-15deg-28MMS-150kmph-HDG fasteners 80 TPSAV set) | MWp | 5 | 1,40,00,000 |
|  | Sub Total |  |  | 1,40,00,000 |
|  | Add GST @18% |  |  | 25,20,000 |
|  | Total |  |  | 1,65,20,000 |
| (Rupees One Crore Sixty Five Lakh Twenty Thousand) only |  |  |  |  |

3. Supply, Installation, Erection & Commissioning of Inverters.

| Sl. No. | Particulars | Unit | Quantity | Amount (in Rs) |
| --- | --- | --- | --- | --- |
| 3.1 | 1 MW, 1500V Central Inverter | MW | 5 | 1,40,00,000 |
| 3.2 | Solar Cables as per TUV 2pfg specification | mtrs | 15000 | 7,68,000 |
| 3.3 | MC4 Pairs- TUV Certified With Male Connector On Positive & Female Connector On Negative Terminals | Nos | 1845 | 1,52,500 |
| 3.4 | Y CONNECTOR PAIRS- TUV Certified With Male Connector On Positive & Female Connector On Negative Terminals | Nos | 750 | 47,500 |
| 3.5 | DC CABLE- 1 Core-185sqmm Alu armored XLPE cable – SMB to Inverter | Mtrs | 2800 | 7,78,840 |
|  | Sub Total |  |  | 1,57,46,840 |
|  | Add GST @18% |  |  | 28,34,431.2 |
|  | Total |  |  | 1,85,81,271.2 |
| (Rupees One Crore Eighty Five Lakh Eighty One Thousand Two Hundred seventy one and two paise) only |  |  |  |  |

- Civil and General Works

| Sl. No. | Particulars | Unit | Quantity | Amount (in Rs) |
| --- | --- | --- | --- | --- |
| 4.1 | Control Room | LS | 1 | 65,00,000 |
| 4.2 | AC Distribution (For control Room, load Distribution) | Nos | 1 | 1,15,600 |
| 4.3 | UPS System for Control Room (10kVA UPS with 3 hour battery backup (SMF VRLA battery) | Nos | 1 | 4,13,100 |
| 4.4 | Lighting arrester – ESE type GI strip for LA – 25x6mm GI strip Earthing line – earthing rod with its compound GI strip – 75x8mm GI strip GI strip – 25x3mm GI strip | LS | 1 | 2,40,000 |
| 4.5 | WMS foundation | No | 1 | 22,949.60 |
| 4.6 | LA foundation | No | 8 | 49,460 |
| 4.7 | SMB mounting stand | No | 135 | 8,74,800 |
| 4.8 | Smoke detectors in control room | No | 2 | 25,920 |
| 4.9 | Manual call in control room | No | 1 | 10,530 |
| 4.10 | Conventional Type Fire alarm panels in control room | No | 2 | 1,48,500 |
| 4.11 | Cables of 2c, 1.5mm, armored, FRLS, copper PVC insulated. | Mtrs | 30 | 27,000 |
| 4.12 | CO2 fire in control room | No | 2 | 66,420 |
| 4.13 | DCP in control room | No | 1 | 36,855 |
| 4.14 | Foam hand type in control room | No | 1 | 21,559.50 |
| 4.15 | Trolley type in control room | No | 1 | 2,02,500 |
| 4.16 | Buckets with stand in control room | No | 1 | 23,000 |
| 4.17 | Closed Circuit Camera with infrared | Set | 1 | 3,91,500 |
|  | Sub Total |  |  | 91,69,694.10 |
|  | Add GST 18% |  |  | 16,50,544.94 |
|  | Total |  |  | 1,08,20,239.04 |
| (Rupees One Crore Eight Lakh Twenty Thousand Two Hundred Thirty Nine and Four Paise) only |  |  |  |  |

- Cables, transformer, switch gears etc.

| Sl. No. | Particulars | Unit | Quantity | Amount (in Rs) |
| --- | --- | --- | --- | --- |
| 5.1 | HT AC CABLES- 3 CoreX1Run-150 sqmm Alu armored XLPE cable – 33kV(E) (from Inverter transformer to HT) | Mtrs | 800 | 17,29,800 |
| 5.2 | AUXILIARY POWER CABLE- For control room from Aux. Trasnformer (3.5CX95sqmm Alu Armoured cable for auxiliary transformer to control room ACDB including cable trench & route marker | Mtrs | 100 | 1,40,000 |
| 5.3 | AUXILIARY CABLES- All auxiliary cables for AC & DC loads (inline and supplied items) | LS | 1 | 4,07,600 |
| 5.4 | CONTROL CABLES- All control and instrumentation cables as per requirement (inline with supplied items) | LS | 1 | 4,60,000 |
| 5.5 | SCADA system for monitoring | MWp | 5 | 5,60,000 |
| 5.6 | Pyranometer – Kipp and Zonen CMP10 with Tilt Disk | Nos | 1 | 1,10,000 |
| 5.7 | Pyranometer – Kipp and Zonen CMP10 with horizontal Disk | Nos | 1 | 85,000 |
| 5.8 | Ambient – PT1000 type | Nos | 2 | 54,320 |
| 5.9 | Module temperature sensor – PT100 with less than 3% accuracy, with 2 numbers for each tilted pyranometer | Nos | 1 | 25,000 |
| 5.10 | Anemometer – wind speed and wind directions | Nos | 1 | 1,50,000 |
| 5.11 | Datalogger – 30 days in built memory storage, file transfer on USB in CSV format with 1min of average data and inbuilt in power bank for 14 days | Nos | 1 | 1,15,000 |
| 5.12 | Inverter Transformer – 5MVA (5000 kVA, 33kV / 0.63kV, ONAN, Off Load Circuit T/C, with cable terminations. LT Side and bare bushing on HT side.) | Nos | 1 | 80,00,000 |
| 5.13 | Auxiliary Transformer, (50kVA, 33kV / 0.433 kV, ONAN) | Nos | 1 | 3,50,000 |
| 5.14 | CT Set with clamps – CT – 100A/5-5Amp, STC-25kVA for 3 Sec, Core-1,CL-5P20,15VA, Core-2,CL-5P20,15VA | Set | 1 | 2,00,000 |
| 5.15 | PT Set with clamps – PT-20kVA, 33kV/√3;110v/√3 | Set | 1 | 2,60,000 |
| 5.16 | 33kV Isolator | Set | 1 | 2,15,000 |
| 5.17 | Circuit Breaker | Set | 1 | 5,35,000 |
| 5.18 | ABT Meter (Main-1 Nos + Check – 1 Nos) 0.2s class, 33kV | Set | 1 | 2,05,000 |
| 5.19 | HT Panel Type 1-1in and 1Out (5MW, 33kV, Outdoor, 12.5kA/1Sec, VCB 630 Amps, Inbuilt Battery Power Pack, Control and Relay Panel functionality included) | Nos | 1 | 2,05,000 |
| 5.20 | UPS distribution (For essential loads) | Nos | 1 | 45,050 |
|  | Sub Total |  |  | 1,48,46,770 |
|  | Add @GST 18% |  |  | 26,72,418.6 |
|  | Total |  |  | 1,75,19,188.6 |
| (Rupees One Crore Seventy Five Lakh Nineteen Thousand One Hundred Eighty Eight and Six Paise) only |  |  |  |  |

- Preliminary and Pre Operative Expenses including IDC & Contigency

| Sl. No. | Particulars | Unit | Quantity | Amount (in Rs) |
| --- | --- | --- | --- | --- |
| 6.1 | Temporary Housing /Godown | LS | 2 | 15,00,000 |
| 6.2 | Consultancy | LS | 1 | 20,00,000 |
| 6.3 | Contingency | LS | 1 | 5,00,000 |
| 6.4 | Tools & Plants | LS | 1 | 10,00,000 |
| 6.5 | Conveyance | LS | 1 | 7,00,000 |
| 6.6 | Jungle Clearance | LS | 1 | 17,80,000 |
|  | Sub Total |  |  | 74,80,000 |
|  | Add GST @18 |  |  | 13,46,400 |
|  | Total |  |  | 88,26,400 |
| (Rupees Eighty Eight Lakh Twenty Six Thousand Four Hundred) only |  |  |  |  |

- 33kV Transmission Line to the nearest sub-station

| Sl. No. | Particulars | Unit | Quantity | Rate (in Rs) | Amount (in Rs) |
| --- | --- | --- | --- | --- | --- |
| 7.1 | SP-49 Regular Three Pole (TP),Double Pole, Single Pole | Nos | 150 | 23793.75 | 35,69,062.5 |
| 7.2 | Conductor ACSR "DOG" | Km | 24 | 80678.15 | 19,36,275.60 |
| 7.3 | MS channel for cross arm 2.250 Mtr Long 100x50x6mm | Kg | 2898 | 203.43 | 5,89,540.14 |
| 7.4 | MS Angle 40x40x6mm, 3.5 Mtr length for diagonal member | Kg | 1225 | 174 | 2,13,150 |
| 7.5 | MS Angle 40X40X6mm, 3.5 Mtr length for horizontal member | Kg | 1225 | 174 | 2,13,150 |
| 7.6 | MS Angle 40x40x6mm for guard bracket | Nos | 80 | 5351.06 | 4,28,084.80 |
| 7.7 | MS Clamp (50x6mm flat), Back Clamp (Single Clamp) | Nos | 300 | 85 | 25,500 |
| 7.8 | MS Clamp (50x6mm flat), Jam Clamp (Double Clamp) | Pairs | 210 | 110 | 23,100 |
| 7.9 | GI Nuts & Bolts 3" & 8" sizes | Kg | 200 | 110 | 22,000 |
| 7.10 | GI Washer of different size | Kg | 130 | 203.43 | 26,445.9 |
| 7.11 | 33 kV Pin Insulator with GI Pin | Nos | 255 | 2674 | 6,81,870 |
| 7.12 | 70 KN Disc (B&S) Single strain insulator | Nos | 300 | 3817 | 11,45,100 |
| 7.13 | Hardware fittings | Nos | 300 | 390 | 1,17,000 |
| 7.14 | HT Stay set complete | Sets | 200 | 1491 | 2,98,200 |
| 7.15 | Stay wire 7/10 SWG | Kg | 700 | 162 | 1,13,400 |
| 7.16 | RCC foundation for Poles | Nos | 150 | 4148.35 | 6,22,253.08 |
| 7.17 | Danger Plate | Nos | 150 | 138 | 20,700 |
| Sub Total |  |  |  |  | 1,00,44,832.02 |
| Add GST @ 18% |  |  |  |  | 18,08,069.76 |
| Total |  |  |  |  | 1,18,52,901.62 |
| (Rupees One Crore Eighteen Lakh Fifty Two Thousand Nine Hundred One and Sixty Two Paise) only |  |  |  |  |  |

Financial analysis has been carried out for selected Mono Crystalline based solar PV module technology. The proposed solar mono crystalline grid connected power project is of 5 MW capacity.

This generation is at grid interconnection point after considering associated losses.

Project cost break-up & means of finance Apart from machinery, installation and commissioning cost, interest during construction, financial institution fees and margin money for working capital is part of project cost. The land cost has been taken negligible as the land has been allocated to DNRE for solar power plant project which belongs to the Government of Nagaland, India. The total project cost and means of finance are summarized.

- Initial Investment in terms of components cost & service Charges per 5MW

| Sl No | Components/Services | Total Cost (Rs. In Lakhs) | % of Total Cost |
| --- | --- | --- | --- |
| 1 | Supply, Installation, Erection and Commissioning of Solar PV Modules | 1663.8 | 66.42% |
| 2 | Module Mounting Structure and associated Civil Works | 165.2 | 6.59% |
| 3 | Supply, Installation, Erection & Commissioning of Inverters | 185.81 | 7.42% |
| 4 | Civil and General Works | 108.2 | 4.32% |
| 5 | Evacuation Cost up to Interconnection Point (Cables and Transformer) | 175.19 | 6.99% |
| 6 | Preliminary and Pre-Operative Expenses including IDC and Contingency, Etc. | 88.26 | 3.52% |
| 7 | 33kV Transmission Line to the nearest sub-station | 118.52 | 4.73% |
|  | Total Capital Cost | 2505 | 100% |

(Rupees Two Thousand Five Hundred and Five Lakhs) only

Conclusion:

The Total expected annual generation of electricity from the proposed 5 MW Mono Crystalline based Solar Power Plant will be about 8.76 MU of Energy for the first year and the Levelized Tariff will be Rs. 3.97 Per KWh. The proposed locations have good Solar Insolation and the project is financially viable.